## Wire Ampacity
Press Tab to Cycle Through Input Variables
| Disclaimer: Calculations are for approximate use only. I assume no liability for the use or misuse of this calculator. | [10 empty] | Source: | http://www.thepanelshop.com/Wire_table.htm
*AC or DC doesn’t matter (up to ~2000 volts).
| *Wire ampacity decreases if: room temperature increases, multiple conductors are bundled, or if conductors are inserted into conduit. | [10 empty] | source: | http://www.ehow.com/how_5859401_calculate-resistance-copper-wire.html
| *Calculations are intended for standard electrical wire. "Welding wire" is treated a bit differently as seen in the table at the bottom. | [10 empty] | source: | http://books.google.com/books?id=fBkUkF2ZRU4C&pg=PA129&lpg=PA129&dq=does+AC+or+DC+affect+ampacity&source=bl&ots=WRDbq9gF0W&sig=2hUuDENs2Cy8EYS92sEiif46o-U&hl=en&sa=X&ei=6wPUUtm3CcTd2QX3oYHgBQ&ved=0CDcQ6AEwAQ#v=onepage&q=does%20AC%20or%20DC%20affect%20ampacity&f=false
*Stranded wire has the same ampacity as solid wire for all practical intents and purposes.
| *Ampacity based on data from 2008 NEC, Table 310.16. | [10 empty] | source: | http://wiki.xtronics.com/index.php/Wire-Gauge_Ampacity | [15 empty] | copper
aluminum
Input Wire Dimensions Below in Red (these dimensions apply to all calculations)
| Wire Material | System Voltage (AC or DC doesn’t matter up to 2000 volts) | AWG Size/gage | Total Length of Wire Used | Ambient Temperature |  | Number of Bundled Wires in Sheath | Rated Wire Temperature (60 °C is normal) |  | AWG and B&S Diameter and Cross-Sectional Areas | [21 empty] | Multiple Conductor Correction Factors |  |  | 1 | 1 | match | the right factor
| (copper or aluminum) | (Volts) | (4/0) - 50 | (ft) | (°F) | (°C) | # | (60, 75, 90 °C) |  |  | Ref # | 22 | [19 empty] | Number of Conductors | Multiply ampacity by factor |  | 2 | 1 | 3 | 1
| copper | 120 | 18 | 10 | 72 | 22.2222 | 3 | 60 |  | AWG or B&S Number | Diameter |  | Cross Section Area |  |  | est 60 C ampacity | [15 empty] | 4-6 | 0.8 |  | 3 | 1 |  | accounts for bundles of wire
[21 empty] | K (constant value for copper) | Wire Area | Wire Area | Resistance | [7 empty] | 7-9 | 0.7 |  | 4 | 0.8
[11 empty] | Inches | mm | Square Inches | Square mm | Circular Mils |  |  | short Length (do not change!) |  | (ft) | ohms/mil-foot | (in^2) | (circular mils) | (ohms) |  |  | ft | in | wire volume |  |  | 10-20 | 0.5 |  | 5 | 0.8
| Wire Characteristics | [8 empty] | (4/0) | 0.46 | 11.68 | 0.1662 | 107.2 | 211600 | 195 | 1 |  |  | 55.1 | 10.4 | 0.0012756 | 1624.09 | 0.35284 | 6.4036 |  | 10 | 120 | 0.15307 | in^3 |  | 21-30 | 0.45 |  | 6 | 0.8
| Wire Diameter | Wire Cross-Section Area |  | Wire Weight | Resistance | Rated Ampacity | Rated Wattage |  |  | (3/0) | 0.4096 | 10.4 | 0.1318 | 85.03 | 167800 | 165 | 2 | Long length (do not change!) |  | (ft) | ohms/mil-foot | (in^2) | (circular mils) | (ohms) | [7 empty] | 31-40 | 0.4 |  | 7 | 0.7
| (in) | (in^2) | (circular mils) | (lb) | (W) | (amp) | (Watts) |  |  | (2/0) | 0.3648 | 9.266 | 0.1045 | 67.43 | 133100 | 145 | 3 |  |  | 243 | 10.4 | 0.0012756 | 1624.09 | 1.5561 | 6.4036 | [6 empty] | 41+ | 0.35 |  | 8 | 0.7
| 0.0403 | 8.252 | 1624.09 | 0.049594 | 0.064595 | 10.6114 | 1273.3691 |  |  | (1/0) | 0.3249 | 8.252 | 0.08289 | 53.48 | 105500 | 125 | 4 | short & shroud length (do not change!) |  | (ft) | ohms/mil-foot | (in^2) | (circular mils) | (ohms) |  |  |  | copper density | 0.324 | lb/in^3 |  |  |  |  | 9 | 0.7
[10 empty] | 1 | 0.2893 | 7.348 | 0.06573 | 42.41 | 83690 | 110 | 5 |  |  | 98 | 10.4 | 0.0012756 | 1624.09 | 0.62755 | 6.4036 |  |  | Aluminum Density | 0.098 | lb/in^3 |  |  |  |  | 10 | 0.5
| Calculated Voltage Drop (Usually this is more important for smaller gage wires) | [8 empty] | 2 | 0.2576 | 6.543 | 0.05123 | 33.63 | 66370 | 95 | 6 | [17 empty] | 11 | 0.5
| Expected Maximum Current | Voltage Drop/Loss |  | Power Loss (heat generated) | Distance before 3% voltage drop |  |  |  |  | 3 | 0.2294 | 5.827 | 0.04134 | 26.27 | 52630 | 82.5 | 7 |  | y = 0.000000x5 - 0.000000x4 + 0.000000x3 - 0.000000x2 + 0.001951x + 13.050349 | [15 empty] | 12 | 0.5
| (amp) | (volts) | (%) | (w) | (ft) |  |  |  |  | 4 | 0.2043 | 5.189 | 0.03278 | 21.15 | 41740 | 70 | 8 |  | R² = 0.999764 | [15 empty] | 13 | 0.5
| 10.6114 | 0.68545 | 0.5712 | 7.2735 | 52.5206 |  |  |  |  | 5 | 0.1879 | 4.62 | 0.026 | 16.77 | 33100 | 62.5 | 9 | [17 empty] | 14 | 0.5
[10 empty] | 6 | 0.162 | 4.115 | 0.02062 | 13.3 | 26250 | 55 | 10 | COPPER |  |  |  | ALUMINUM | [12 empty] | 15 | 0.5
[10 empty] | 7 | 0.1443 | 3.665 | 0.01635 | 10.55 | 20820 | 47.5 | 11 | Conductor | Allowable |  |  | Allowable |  |  | Conductor | [9 empty] | 16 | 0.5
[10 empty] | 8 | 0.1285 | 3.264 | 0.01297 | 8.366 | 16510 | 40 | 12 | Size | Ampacities* |  |  | Ampacities* |  |  | Size | [6 empty] | MATERIAL FACTOR |  |  | 17 | 0.5
[10 empty] | 9 | 0.1144 | 2.906 | 0.01028 | 6.634 | 13090 | 35.331 | 13 | AWG or kcmil | 60°C | 75°C | 90°C | 60°C | 75°C | 90°C | AWG or kcmil | 1.2041 | 1.3588 |  | 1.212 | 1.3797 |  | 0.78012 |  |  | 18 | 0.5
[9 empty] | #NAME? | 10 | 0.1019 | 2.588 | 0.008156 | 5.261 | 10380 | 30.6772 | 14 |  |  | TYPES THWN, RHW, USE | TYPES THWN-2, USE-2, XHHW-2, XHHW, RHW-2, RHH |  | TYPES THWN, RHW, USE | TYPES THWN-2, USE-2, XHHW-2, XHHW, RHW-2, RHH |  | CONDUCTOR RATED TEMPERATURE FACTOR | [8 empty] | 19 | 0.5
[10 empty] | 11 | 0.09074 | 2.305 | 0.006467 | 4.172 | 8234 | 26.6421 | 15 | 8 | 40 | 50 | 55 | 30 | 40 | 45 | 8 | 1.25 | 1.375 |  | 1.3333 | 1.5 |  | 0.75 | 0.8 | 0.81818 | 20 | 0.45
[10 empty] | 12 | 0.08081 | 2.053 | 0.005129 | 3.309 | 6530 | 23.1342 | 16 | 6 | 55 | 65 | 75 | 40 | 50 | 60 | 6 | 1.1818 | 1.3636 |  | 1.25 | 1.5 |  | 0.72727 | 0.76923 | 0.8 | 21 | 0.45
[10 empty] | 13 | 0.07196 | 1.828 | 0.004067 | 2.624 | 5178 | 20.0867 | 17 | 4 | 70 | 85 | 95 | 55 | 65 | 75 | 4 | 1.2143 | 1.3571 |  | 1.1818 | 1.3636 |  | 0.78571 | 0.76471 | 0.78947 | 22 | 0.45
[10 empty] | 14 | 0.06408 | 1.628 | 0.003225 | 2.081 | 4107 | 17.4434 | 18 | 2 | 95 | 115 | 130 | 75 | 90 | 100 | 2 | 1.2105 | 1.3684 |  | 1.2 | 1.3333 |  | 0.78947 | 0.78261 | 0.76923 | 23 | 0.45
[10 empty] | 15 | 0.05707 | 1.45 | 0.002558 | 1.65 | 3257 | 15.1465 | 19 | 1 | 110 | 130 | 150 | 85 | 100 | 115 | 1 | 1.1818 | 1.3636 |  | 1.1765 | 1.3529 |  | 0.77273 | 0.76923 | 0.76667 | 24 | 0.45
[10 empty] | 16 | 0.05082 | 1.291 | 0.002028 | 1.309 | 2583 | 13.1523 | 20 | (1/0) | 125 | 150 | 170 | 100 | 120 | 135 | 2000-01-01 | 1.2 | 1.36 |  | 1.2 | 1.35 |  | 0.8 | 0.8 | 0.79412 | 25 | 0.45
[10 empty] | 17 | 0.04526 | 1.15 | 0.001609 | 1.038 | 2048 | 11.419 | 21 | (2/0) | 145 | 175 | 195 | 115 | 135 | 150 | 2000-02-01 | 1.2069 | 1.3448 |  | 1.1739 | 1.3043 |  | 0.7931 | 0.77143 | 0.76923 | 26 | 0.45
[10 empty] | 18 | 0.0403 | 1.024 | 0.001276 | 0.8231 | 1600 | 9.8254 | 22 | (3/0) | 165 | 200 | 225 | 130 | 155 | 175 | 2000-03-01 | 1.2121 | 1.3636 |  | 1.1923 | 1.3462 |  | 0.78788 | 0.775 | 0.77778 | 27 | 0.45
[10 empty] | 19 | 0.03589 | 0.9116 | 0.001012 | 0.6527 | 1288 | 8.6097 | 23 | (4/0) | 195 | 230 | 260 | 150 | 180 | 205 | 2000-04-01 | 1.1795 | 1.3333 |  | 1.2 | 1.3667 |  | 0.76923 | 0.78261 | 0.78846 | 28 | 0.45
[10 empty] | 20 | 0.03196 | 0.8118 | 0.0008023 | 0.5176 | 1022 | 7.4785 | 24 | [17 empty] | 29 | 0.45
[10 empty] | 21 | 0.02846 | 0.7229 | 0.0006363 | 0.4105 | 810.1 | 6.4919 | 25 | [17 empty] | 30 | 0.45
[10 empty] | 22 | 0.02535 | 0.6439 | 0.0005046 | 0.3256 | 642.4 | 5.6369 | 26 | [17 empty] | 31 | 0.4
[10 empty] | 23 | 0.02257 | 0.5733 | 0.0004001 | 0.2582 | 509.5 | [8 empty] | http://www.safecoelectric.com/images/resources_pdf/NEC2008%20Table%20310.16.pdf | [10 empty] | 32 | 0.4
[10 empty] | 24 | 0.0201 | 0.5105 | 0.0003173 | 0.2047 | 404 | [19 empty] | 33 | 0.4
[10 empty] | 25 | 0.0179 | 0.4547 | 0.0002517 | 0.1624 | 320.4 |  |  |  | Factor | [15 empty] | 34 | 0.4
[10 empty] | 26 | 0.01584 | 0.4049 | 0.0001996 | 0.1288 | 254.1 |  |  |  | CU |  |  | AL | [12 empty] | 35 | 0.4
[10 empty] | 27 | 0.0142 | 0.3607 | 0.0001583 | 0.1021 | 201.5 |  |  |  | 60 | 75 | 90 | 60 | 75 | 90 | [5 empty] | cu | al |  |  |  | 36 | 0.4
[10 empty] | 28 | 0.01264 | 0.3211 | 0.0001255 | 0.08098 | 159.8 |  |  |  | 1 | 1.2041 | 1.3588 | 1 | 1.212 | 1.3797 |  |  |  |  | 60 | 1.08 | 0.84253 |  |  |  | 37 | 0.4
[10 empty] | 29 | 0.01126 | 0.286 | 9.954e-05 | 0.06422 | 126.7 | [13 empty] | 75 | 1.2643 | 0.99277 |  |  |  | 38 | 0.4
[10 empty] | 30 | 0.01003 | 0.2548 | 7.894e-05 | 0.05093 | 100.5 |  |  |  | 1.08 | 1.2643 | 1.4132 | 1.08 | 1.2726 | 1.4349 | matched & multplied by factor |  | 4 |  | 90 | 1.4132 | 1.1194 |  |  |  | 39 | 0.4
[10 empty] | 31 | 0.008928 | 0.2268 | 6.26e-05 | 0.04039 | 79.7 |  |  | Ambient | 1.08 | 1.05 | 1.04 | 1.08 | 1.05 | 1.04 | matched | 3 | [8 empty] | 40 | 0.4
[10 empty] | 32 | 0.00795 | 0.2019 | 4.964e-05 | 0.03023 | 63.21 |  |  | 6 | 1.32 | 1.2 | 1.16 | 1.32 | 1.2 | 1.16 |  | 22 | rounded | 1 |  | SUM table |  | 5 |  |  | 41 | 0.35
[10 empty] | 33 | 0.00708 | 0.1796 | 3.944e-05 | 0.02545 | 50.22 |  |  | 7 | 1.32 | 1.2 | 1.16 | 1.32 | 1.2 | 1.16 |  | 17 | indexed | 2 |  | 1.08 | 0 |  |  |  | 42 | 0.35
[10 empty] | 34 | 0.006305 | 0.1601 | 3.122e-05 | 0.02014 | 39.75 |  |  | 8 | 1.32 | 1.2 | 1.16 | 1.32 | 1.2 | 1.16 | [5 empty] | 0 | 0 |  |  |  | 43 | 0.35
[10 empty] | 35 | 0.005615 | 0.1426 | 2.476e-05 | 0.01597 | 31.52 |  |  | 9 | 1.32 | 1.2 | 1.16 | 1.32 | 1.2 | 1.16 | [5 empty] | 0 | 0 |  |  |  | 44 | 0.35
[10 empty] | 36 | 0.005 | 0.127 | 1.963e-05 | 0.01267 | 25 |  |  | 10 | 1.32 | 1.2 | 1.16 | 1.32 | 1.2 | 1.16 | [10 empty] | 45 | 0.35
[10 empty] | 37 | 0.004453 | 0.1131 | 1.557e-05 | 0.01005 | 19.83 |  |  | 11 | 1.32 | 1.2 | 1.16 | 1.32 | 1.2 | 1.16 | [6 empty] | 1.08 | 6 |  |  | 46 | 0.35
[10 empty] | 38 | 0.003965 | 0.1007 | 1.235e-05 | 0.00797 | 15.72 |  |  | 12 | 1.24 | 1.15 | 1.12 | 1.24 | 1.15 | 1.12 | [5 empty] | final factor (accoutns for material, temp rating, and ambent temp) |  |  |  |  | 47 | 0.35
[10 empty] | 39 | 0.003531 | 0.0897 | 9.79e-06 | 0.00632 | 12.47 |  |  | 13 | 1.24 | 1.15 | 1.12 | 1.24 | 1.15 | 1.12 | [10 empty] | 48 | 0.35
[10 empty] | 40 | 0.003145 | 0.0799 | 7.77e-06 | 0.00501 | 9.888 |  |  | 14 | 1.24 | 1.15 | 1.12 | 1.24 | 1.15 | 1.12 | [10 empty] | 49 | 0.35
[10 empty] | 41 | 0.0028 | 0.0711 | 6.16e-06 | 0.00397 | 7.842 |  |  | 15 | 1.24 | 1.15 | 1.12 | 1.24 | 1.15 | 1.12 | [10 empty] | 50 | 0.35
[10 empty] | 42 | 0.002494 | 0.0633 | 4.88e-06 | 0.00315 | 6.219 |  |  | 16 | 1.16 | 1.1 | 1.08 | 1.16 | 1.1 | 1.08
[10 empty] | 43 | 0.002221 | 0.0564 | 3.87e-06 | 0.0025 | 4.932 |  |  | 17 | 1.16 | 1.1 | 1.08 | 1.16 | 1.1 | 1.08
[10 empty] | 44 | 0.001978 | 0.0502 | 3.07e-06 | 0.00198 | 3.911 |  |  | 18 | 1.16 | 1.1 | 1.08 | 1.16 | 1.1 | 1.08
[10 empty] | 45 | 0.001761 | 0.0447 | 2.44e-06 | 0.00157 | 3.102 |  |  | 19 | 1.16 | 1.1 | 1.08 | 1.16 | 1.1 | 1.08
[10 empty] | 46 | 0.001568 | 0.0398 | 1.93e-06 | 0.00125 | 2.46 |  |  | 20 | 1.16 | 1.1 | 1.08 | 1.16 | 1.1 | 1.08
[10 empty] | 47 | 0.001397 | 0.0355 | 1.53e-06 | 0.00099 | 1.951 |  |  | 21 | 1.08 | 1.05 | 1.04 | 1.08 | 1.05 | 1.04
[10 empty] | 48 | 0.001244 | 0.0316 | 1.22e-06 | 0.00078 | 1.547 |  |  | 22 | 1.08 | 1.05 | 1.04 | 1.08 | 1.05 | 1.04
[10 empty] | 49 | 0.001107 | 0.0281 | 9.6e-07 | 0.00062 | 1.227 |  |  | 23 | 1.08 | 1.05 | 1.04 | 1.08 | 1.05 | 1.04
[10 empty] | 50 | 0.000986 | 0.0251 | 7.6e-07 | 0.00049 | 0.973 |  |  | 24 | 1.08 | 1.05 | 1.04 | 1.08 | 1.05 | 1.04
[18 empty] | 25 | 1.08 | 1.05 | 1.04 | 1.08 | 1.05 | 1.04
[18 empty] | 26 | 1 | 1 | 1 | 1 | 1 | 1
[18 empty] | 27 | 1 | 1 | 1 | 1 | 1 | 1
[18 empty] | 28 | 1 | 1 | 1 | 1 | 1 | 1
[18 empty] | 29 | 1 | 1 | 1 | 1 | 1 | 1
[18 empty] | 30 | 1 | 1 | 1 | 1 | 1 | 1
[18 empty] | 31 | 0.91 | 0.94 | 0.96 | 0.91 | 0.94 | 0.96
[18 empty] | 32 | 0.91 | 0.94 | 0.96 | 0.91 | 0.94 | 0.96
[18 empty] | 33 | 0.91 | 0.94 | 0.96 | 0.91 | 0.94 | 0.96
[18 empty] | 34 | 0.91 | 0.94 | 0.96 | 0.91 | 0.94 | 0.96
[18 empty] | 35 | 0.91 | 0.94 | 0.96 | 0.91 | 0.94 | 0.96
[18 empty] | 36 | 0.82 | 0.88 | 0.91 | 0.82 | 0.88 | 0.91
[18 empty] | 37 | 0.82 | 0.88 | 0.91 | 0.82 | 0.88 | 0.91
[18 empty] | 38 | 0.82 | 0.88 | 0.91 | 0.82 | 0.88 | 0.91
[18 empty] | 39 | 0.82 | 0.88 | 0.91 | 0.82 | 0.88 | 0.91
[18 empty] | 40 | 0.82 | 0.88 | 0.91 | 0.82 | 0.88 | 0.91
[18 empty] | 41 | 0.71 | 0.82 | 0.87 | 0.71 | 0.82 | 0.87
[18 empty] | 42 | 0.71 | 0.82 | 0.87 | 0.71 | 0.82 | 0.87
[18 empty] | 43 | 0.71 | 0.82 | 0.87 | 0.71 | 0.82 | 0.87
[18 empty] | 44 | 0.71 | 0.82 | 0.87 | 0.71 | 0.82 | 0.87
[18 empty] | 45 | 0.71 | 0.82 | 0.87 | 0.71 | 0.82 | 0.87
[18 empty] | 46 | 0.58 | 0.75 | 0.82 | 0.58 | 0.75 | 0.82
[18 empty] | 47 | 0.58 | 0.75 | 0.82 | 0.58 | 0.75 | 0.82
[18 empty] | 48 | 0.58 | 0.75 | 0.82 | 0.58 | 0.75 | 0.82
[18 empty] | 49 | 0.58 | 0.75 | 0.82 | 0.58 | 0.75 | 0.82
[18 empty] | 50 | 0.58 | 0.75 | 0.82 | 0.58 | 0.75 | 0.82
[18 empty] | 51 | 0.41 | 0.67 | 0.76 | 0.41 | 0.67 | 0.76
[18 empty] | 52 | 0.41 | 0.67 | 0.76 | 0.41 | 0.67 | 0.76
[18 empty] | 53 | 0.41 | 0.67 | 0.76 | 0.41 | 0.67 | 0.76
[18 empty] | 54 | 0.41 | 0.67 | 0.76 | 0.41 | 0.67 | 0.76
[18 empty] | 55 | 0.41 | 0.67 | 0.76 | 0.41 | 0.67 | 0.76
[18 empty] | 56 | 0 | 0.58 | 0.71 | 0 | 0.58 | 0.71
[18 empty] | 57 | 0 | 0.58 | 0.71 | 0 | 0.58 | 0.71
[18 empty] | 58 | 0 | 0.58 | 0.71 | 0 | 0.58 | 0.71
[18 empty] | 59 | 0 | 0.58 | 0.71 | 0 | 0.58 | 0.71
[18 empty] | 60 | 0 | 0.58 | 0.71 | 0 | 0.58 | 0.71
[18 empty] | 61 | 0 | 0.33 | 0.58 | 0 | 0.33 | 0.58
[18 empty] | 62 | 0 | 0.33 | 0.58 | 0 | 0.33 | 0.58
[18 empty] | 63 | 0 | 0.33 | 0.58 | 0 | 0.33 | 0.58
[18 empty] | 64 | 0 | 0.33 | 0.58 | 0 | 0.33 | 0.58
[18 empty] | 65 | 0 | 0.33 | 0.58 | 0 | 0.33 | 0.58
[18 empty] | 66 | 0 | 0.33 | 0.58 | 0 | 0.33 | 0.58
[18 empty] | 67 | 0 | 0.33 | 0.58 | 0 | 0.33 | 0.58
[18 empty] | 68 | 0 | 0.33 | 0.58 | 0 | 0.33 | 0.58
[18 empty] | 69 | 0 | 0.33 | 0.58 | 0 | 0.33 | 0.58
[18 empty] | 70 | 0 | 0.33 | 0.58 | 0 | 0.33 | 0.58
[18 empty] | 71 | 0 | 0 | 0.41 | 0 | 0 | 0.41
[18 empty] | 72 | 0 | 0 | 0.41 | 0 | 0 | 0.41
[18 empty] | 73 | 0 | 0 | 0.41 | 0 | 0 | 0.41
[18 empty] | 74 | 0 | 0 | 0.41 | 0 | 0 | 0.41
[18 empty] | 75 | 0 | 0 | 0.41 | 0 | 0 | 0.41
[18 empty] | 76 | 0 | 0 | 0.41 | 0 | 0 | 0.41
[18 empty] | 77 | 0 | 0 | 0.41 | 0 | 0 | 0.41
[18 empty] | 78 | 0 | 0 | 0.41 | 0 | 0 | 0.41
[18 empty] | 79 | 0 | 0 | 0.41 | 0 | 0 | 0.41
[18 empty] | 80 | 0 | 0 | 0.41 | 0 | 0 | 0.41
CABLE SIZES - NOT DRAWN TO SCALE